Amendment to Request for Proposals

| Issued By: University of Baltimore Department of Procurement 1420 North Charles Street Baltimore, MD 21201 Ms. Toni Wallington Telephone: 410-837-5130 FAX: 410-837-5492 e-mail: twallington@ubalt.edu | AMENDMENT NUMBER ONE RFP Number: No. UB 17-W-08 Amendment Issued: October 7, 2016 RFP Due Date and Time: October 24, 2016 by 3:00 PM |
| --- | --- |
| To: Offeror |  |

AMENDMENT NUMBER ONE

To RFP for

Fire Alarm/Sprinkler Syst. & Fire Pump Test

For

The University of Baltimore

Change the RFP specifications, terms and conditions in the following particulars only.

A pre-proposal conference was held on October 4, 2016.  A brief summary of the RFP purpose and Process was discussed.

The following questions were asked at the pre-proposal conference:

QUESTION:  	The contractor must provide two inspections per year per the RFP.  How much of the inspection is needed for the first visit	and the second visit?

ANSWER:   	Inspections must be in accordance with NFP72 standards.  The only stipulation is that any audible/visual testing must be completed during non-school times (ie, the first two weeks in January).

QUESTION:  	The Fire Pumps are to be tested quarterly, what is required?

ANSWER:	According to NFPA25, fire pumps must be tested on both a monthly and annual basis to ensure that they will perform as designed.  These two different tests are referred to as monthly “churn” test and an annual flow test.

ANNUAL FIRE PUMP FLOW TEST

The fire pump flow test is required by NFPA25 to be conducted once a year in order to measure the pump’s flow and pressure.  The test should be performed by attaching hoses to the discharge test header.  The hoses are to run to a safe location where the flow of water will cause no damage. Pressure readings are to be taken as the pump runs through its various stages and the results are to recorded and compared to results from previous years.  If there is a significant reduction in the pump’s performance, further examination may be needed to make the necessary repairs.

MONTHLY FIRE PUMP CHURN (aka No Flow) Test

The 2011 Edition of NFPA 25 requires electric motor driven fire pumps to be operated monthly.  Recently, this code has been enforced more strictly.  The monthly churn test requires electric powered pumps to be tested as follows:

- Run pump for a minimum of 10 minutes.

- Record the system suction & discharge pressure gauge readings.

- Check the pump packing glands for slight discharge.

- Adjust glands nuts; if necessary.

- Check for unusual noise or vibration.

- Check packing boxes, bearings or pump causing for overheating.

- Record the pump starting pressure.

- Interpret results.

SEE ATTACHED DOCUMENT FOR ADDITIONAL FIRE PUMP CHURN TEST PROCEDURES.

ALL OTHER SPECIFICATIONS, TERMS AND CONDITIONS REMAIN THE SAME.

ALL OFFERORS MUST ACKNOWLEDGE THE RECEIPT OF ALL AMENDMENTS ISSUED.

End of Amendment Number One

| TO BE COMPLETED BY THE FIRM OFFERING A PROPOSAL |
| --- |
| NAME AND ADDRESS OF OFFEROR FEI Number: _____________ | SIGNATURE OF PERSON AUTHORIZED TO SIGN QUOTATION | DATE OF QUOTATION |
|  | SIGNER’S NAME AND TITLE | TELEPHONE No. |